{"text_format":"3","workbook":"xls","n_sheets":9,"sheets":["위생기구일람표","동시사용률","균등표","급수급탕지관의관경선정표","환탕지관의관경선정표","급수급탕횡주관및입상관경표","오배수관의횡지관경선정표","오배수관의횡주관경선정표","오배수관의입상관경선정표"],"not_rendered":{"external_links":1,"defined_names":9},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"위생기구일람표","index":0,"n_rows":12,"n_cols":9,"rows_kept":12,"flags":["formulas_cached_only"]}
["위생기구명","구분","단축명","급수","급탕","오배수","상당관수","fu","fuD"]
["대변기","세정밸브","-",25,"-",100,4,10,8]
["대변기","Low Tank","-",15,"-",100,1,5,4]
["소변기","일반수전","-",15,"-",40,1,4,4]
["세면기","일반수전","-",15,15,32,1,1,1]
["샤워기","샤워수전","-",20,20,2,4,4,"-"]
["욕조","샤워수전","-",20,20,75,2,4,6]
["청소싱크","일반수전","-",20,20,75,2,4,5]
["주방싱크","일반수전","-",20,20,50,2,3,5]
["탕비싱크","일반수전","-",20,20,50,3,4,"-"]
["바닥배수구","청소용","-","-","-",75,"-","-",5]
["비대","일반수전","-",20,20,75,2,3,"-"]

{"sheet":"동시사용률","index":1,"n_rows":15,"n_cols":2,"rows_kept":15,"flags":["formulas_cached_only"]}
["상당수","동시사용률"]
[2,100]
[3,80]
[4,75]
[5,70]
[10,53]
[15,48]
[20,44]
[30,40]
[50,36]
[99,34]
[10,33]
[150,32]
[200,31]
[350,30]

{"sheet":"균등표","index":2,"n_rows":12,"n_cols":2,"rows_kept":12,"flags":["formulas_cached_only"]}
["관경","상당수"]
[15,1]
[20,2]
[25,3.7]
[32,7.2]
[40,11]
[50,20]
[65,31]
[80,54]
[100,107]
[125,188]
[150,297]

{"sheet":"급수급탕지관의관경선정표","index":3,"n_rows":12,"n_cols":3,"rows_kept":12,"flags":["formulas_cached_only"]}
["상당수","사무실","극장"]
[15,1,1]
[20,2,2]
[25,5,3.7]
[32,14,7.2]
[40,26,11]
[50,55,20]
[65,90,31]
[80,190,54]
[100,350,107]
[125,null,188]
[150,null,297]

{"sheet":"환탕지관의관경선정표","index":4,"n_rows":10,"n_cols":3,"rows_kept":10,"flags":["formulas_cached_only"]}
["환탕지관경","급탕지관경","극장"]
[20,20]
[20,32]
[25,40]
[32,50]
[40,65]
[40,80]
[50,100]
[80,125]
[100,150]

{"sheet":"급수급탕횡주관및입상관경표","index":5,"n_rows":16,"n_cols":7,"rows_kept":16,"flags":["formulas_cached_only"]}
["관경","부하급수","부하급탕","유량급수","유량급탕","유속급수","유속급탕"]
[15,"-","-",6.5,4,0.52,0.32]
[20,"-","-",15,8.2,0.62,0.38]
[25,10,5,28,17,0.72,0.43]
[32,20,12,52,32,0.85,0.47]
[40,35,23,80,48,0.95,0.58]
[50,95,45,160,90,1.2,0.64]
[65,250,105,280,175,1.3,0.78]
[80,455,245,450,280,1.4,0.9]
[100,1000,600,800,550,1.5,1.08]
[125,2130,1300,1300,950,1.5,1.2]
[150,"-",2700,1800,1500,1.5,1.33]
[200,"-","-",3000,3000,1.5,1.5]
[250,"-","-",4500,4500,1.5,1.5]
[300,"-","-",6500,6500,1.5,1.5]
[350,"-","-",8000,8000,1.5,1.5]

{"sheet":"오배수관의횡지관경선정표","index":6,"n_rows":7,"n_cols":2,"rows_kept":7,"flags":["formulas_cached_only"]}
["관경","fuD"]
[50,6]
[75,20]
[100,160]
[125,360]
[150,620]
[200,1400]

{"sheet":"오배수관의횡주관경선정표","index":7,"n_rows":8,"n_cols":2,"rows_kept":8,"flags":["formulas_cached_only"]}
["관경","fuD"]
[75,20]
[100,180]
[125,390]
[150,700]
[200,1400]
[250,2500]
[300,3900]

{"sheet":"오배수관의입상관경선정표","index":8,"n_rows":7,"n_cols":2,"rows_kept":7,"flags":["formulas_cached_only"]}
["관경","fuD"]
[50,24]
[75,63]
[100,560]
[125,1100]
[150,1900]
[200,3600]